## Sheet1
Effective: 1031 rev.2
Automatic Capacitor Bank Sizing
SELECTING AN AUTOMATIC CAPACITOR SIZE |  |  |  | Example: How much kVAR is required to correct an entire
480V system to a 90% power factor when the peak kilowatt
The following calculator is used to determine the capacitor kVAR |  |  |  | demand month was 620kW at a 65% power factor?
required to improve PF of a single load or entire power system.
Actual power factor, peak kilowatt demand, desired PF and |  |  |  | Formula: kVAR = kW x kW FACTOR
system voltage are required. The best source for this information
is the monthly utility bill or other local monitoring equipment. A |  |  |  | From the kW FACTOR calculator below , the FACTOR
calculation of each months data for a 12 month period is |  |  |  | is 0.685
recommended to determine the maximum kVAR required.
Therefore: kVAR = 620 x .685 = 425
| Existing P.F (%) |  | 90
| Desired P.F. (%) |  | 95
| Load (kW) |  | 1324
|  | Kilowatt Factor |  | 0.15564
|  | Required kVAR |  | 206.0647

## Voltage
Voltage
180
19

## PF Table
Schneider Canada Capacitor Division
Automatic Capacitor Bank Sizing
| SELECTING AN AUTOMATIC CAPACITOR SIZE | [11 empty] | Example: How much kVAR is required to correct an entire
480V system to a 90% power factor when the peak kilowatt
| The following table is used to determine the capacitor kVAR | [11 empty] | demand month was 620kW at a 65% power factor?
required to improve PF of a single load or entire power system.
| Actual power factor, peak kilowatt demand and desired PF are | [11 empty] | Use the formula: kVAR = kW x kW FACTOR
required. The best source for this information is the monthly
| utility bill or other local monitoring equipment. A calculation of | [11 empty] | From the kW FACTOR Table below, find the FACTOR
| each months data for a 12 month period is recommended to | [11 empty] | that applies to a system with an original PF of 65% and
| determine the maximum kVAR required. | [11 empty] | a desired PF of 90%. This FACTOR is read to be 0.685.
Therefore: kVAR = 620 x .685 = 425kVAR
kW FACTOR TABLE
Desired PF in Percent
|  | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100
| 50 | 0.98205 | 1.0081 | 1.034 | 1.06 | 1.0861 | 1.1123 | 1.1387 | 1.1653 | 1.1923 | 1.2197 | 1.2477 | 1.2764 | 1.3061 | 1.3368 | 1.3691 | 1.4034 | 1.4404 | 1.4814 | 1.529 | 1.5896 | 1.7321
| 51 | 0.93662 | 0.96263 | 0.98861 | 1.0146 | 1.0407 | 1.0669 | 1.0933 | 1.1199 | 1.1469 | 1.1743 | 1.2023 | 1.231 | 1.2606 | 1.2914 | 1.3237 | 1.3579 | 1.3949 | 1.436 | 1.4836 | 1.5441 | 1.6866
| 52 | 0.89263 | 0.91864 | 0.94462 | 0.97062 | 0.99669 | 1.0229 | 1.0493 | 1.0759 | 1.1029 | 1.1303 | 1.1583 | 1.187 | 1.2166 | 1.2474 | 1.2797 | 1.3139 | 1.351 | 1.392 | 1.4396 | 1.5001 | 1.6426
| 53 | 0.85 | 0.87601 | 0.90199 | 0.92799 | 0.95406 | 0.98025 | 1.0066 | 1.0333 | 1.0603 | 1.0877 | 1.1157 | 1.1444 | 1.174 | 1.2048 | 1.237 | 1.2713 | 1.3083 | 1.3494 | 1.3969 | 1.4575 | 1.6
| 54 | 0.80864 | 0.83465 | 0.86063 | 0.88663 | 0.9127 | 0.93889 | 0.96527 | 0.99191 | 1.0189 | 1.0463 | 1.0743 | 1.103 | 1.1326 | 1.1634 | 1.1957 | 1.23 | 1.267 | 1.308 | 1.3556 | 1.4161 | 1.5586
| 55 | 0.76848 | 0.79449 | 0.82048 | 0.84648 | 0.87255 | 0.89874 | 0.92512 | 0.95176 | 0.97874 | 1.0062 | 1.0342 | 1.0629 | 1.0925 | 1.1233 | 1.1555 | 1.1898 | 1.2268 | 1.2679 | 1.3154 | 1.376 | 1.5185
| 56 | 0.72945 | 0.75546 | 0.78145 | 0.80745 | 0.83351 | 0.85971 | 0.88609 | 0.91272 | 0.93971 | 0.96714 | 0.99513 | 1.0238 | 1.0535 | 1.0842 | 1.1165 | 1.1508 | 1.1878 | 1.2288 | 1.2764 | 1.337 | 1.4795
| 57 | 0.69148 | 0.71749 | 0.74348 | 0.76948 | 0.79555 | 0.82174 | 0.84812 | 0.87476 | 0.90174 | 0.92917 | 0.95716 | 0.98587 | 1.0155 | 1.0463 | 1.0785 | 1.1128 | 1.1498 | 1.1909 | 1.2384 | 1.299 | 1.4415
| 58 | 0.65451 | 0.68052 | 0.70651 | 0.73251 | 0.75857 | 0.78477 | 0.81115 | 0.83779 | 0.86477 | 0.8922 | 0.92019 | 0.9489 | 0.97851 | 1.0093 | 1.0416 | 1.0758 | 1.1128 | 1.1539 | 1.2015 | 1.262 | 1.4045
| 59 | 0.61848 | 0.64449 | 0.67048 | 0.69648 | 0.72254 | 0.74874 | 0.77511 | 0.80175 | 0.82874 | 0.85616 | 0.88416 | 0.91287 | 0.94248 | 0.97325 | 1.0055 | 1.0398 | 1.0768 | 1.1179 | 1.1654 | 1.226 | 1.3685
| 60 | 0.58333 | 0.60935 | 0.63533 | 0.66133 | 0.6874 | 0.71359 | 0.73997 | 0.76661 | 0.79359 | 0.82102 | 0.84901 | 0.87772 | 0.90734 | 0.93811 | 0.97038 | 1.0046 | 1.0417 | 1.0827 | 1.1303 | 1.1908 | 1.3333
| 61 | 0.54902 | 0.57503 | 0.60101 | 0.62701 | 0.65308 | 0.67927 | 0.70565 | 0.73229 | 0.75928 | 0.7867 | 0.8147 | 0.84341 | 0.87302 | 0.90379 | 0.93607 | 0.97033 | 1.0074 | 1.0484 | 1.096 | 1.1565 | 1.299
| 62 | 0.51549 | 0.5415 | 0.56748 | 0.59348 | 0.61955 | 0.64574 | 0.67212 | 0.69876 | 0.72574 | 0.75317 | 0.78116 | 0.80987 | 0.83949 | 0.87026 | 0.90254 | 0.9368 | 0.97382 | 1.0149 | 1.0624 | 1.123 | 1.2655
| 63 | 0.48269 | 0.5087 | 0.53469 | 0.56069 | 0.58675 | 0.61295 | 0.63933 | 0.66596 | 0.69295 | 0.72038 | 0.74837 | 0.77708 | 0.80669 | 0.83747 | 0.86974 | 0.90401 | 0.94102 | 0.98207 | 1.0296 | 1.0902 | 1.2327
| 64 | 0.45059 | 0.4766 | 0.50258 | 0.52858 | 0.55465 | 0.58084 | 0.60722 | 0.63386 | 0.66084 | 0.68827 | 0.71626 | 0.74497 | 0.77459 | 0.80536 | 0.83763 | 0.8719 | 0.90892 | 0.94996 | 0.99753 | 1.0581 | 1.2006
t | 65 | 0.41913 | 0.44514 | 0.47113 | 0.49713 | 0.52319 | 0.54939 | 0.57576 | 0.6024 | 0.62939 | 0.65681 | 0.68481 | 0.71352 | 0.74313 | 0.7739 | 0.80618 | 0.84045 | 0.87746 | 0.91851 | 0.96607 | 1.0266 | 1.1691
n
e | 66 | 0.38828 | 0.41429 | 0.44028 | 0.46628 | 0.49235 | 0.51854 | 0.54492 | 0.57156 | 0.59854 | 0.62597 | 0.65396 | 0.68267 | 0.71228 | 0.74306 | 0.77533 | 0.8096 | 0.84661 | 0.88766 | 0.93522 | 0.99579 | 1.1383
c | 67 | 0.358 | 0.38401 | 0.41 | 0.436 | 0.46207 | 0.48826 | 0.51464 | 0.54128 | 0.56826 | 0.59569 | 0.62368 | 0.65239 | 0.682 | 0.71278 | 0.74505 | 0.77932 | 0.81633 | 0.85738 | 0.90494 | 0.96551 | 1.108
r | 68 | 0.32825 | 0.35427 | 0.38025 | 0.40625 | 0.43232 | 0.45851 | 0.48489 | 0.51153 | 0.53851 | 0.56594 | 0.59393 | 0.62264 | 0.65225 | 0.68303 | 0.7153 | 0.74957 | 0.78659 | 0.82763 | 0.87519 | 0.93576 | 1.0783
e | 69 | 0.299 | 0.32501 | 0.35099 | 0.37699 | 0.40306 | 0.42925 | 0.45563 | 0.48227 | 0.50926 | 0.53668 | 0.56468 | 0.59339 | 0.623 | 0.65377 | 0.68605 | 0.72031 | 0.75733 | 0.79838 | 0.84594 | 0.90651 | 1.049
P | 70 | 0.2702 | 0.29622 | 0.3222 | 0.3482 | 0.37427 | 0.40046 | 0.42684 | 0.45348 | 0.48046 | 0.50789 | 0.53588 | 0.56459 | 0.59421 | 0.62498 | 0.65725 | 0.69152 | 0.72854 | 0.76958 | 0.81715 | 0.87771 | 1.0202
n | 71 | 0.24183 | 0.26785 | 0.29383 | 0.31983 | 0.3459 | 0.37209 | 0.39847 | 0.42511 | 0.45209 | 0.47952 | 0.50751 | 0.53622 | 0.56584 | 0.59661 | 0.62888 | 0.66315 | 0.70017 | 0.74121 | 0.78877 | 0.84934 | 0.99183
i | 72 | 0.21385 | 0.23987 | 0.26585 | 0.29185 | 0.31792 | 0.34411 | 0.37049 | 0.39713 | 0.42411 | 0.45154 | 0.47953 | 0.50824 | 0.53785 | 0.56863 | 0.6009 | 0.63517 | 0.67219 | 0.71323 | 0.76079 | 0.82136 | 0.96385
| 73 | 0.18623 | 0.21224 | 0.23822 | 0.26422 | 0.29029 | 0.31648 | 0.34286 | 0.3695 | 0.39649 | 0.42391 | 0.45191 | 0.48062 | 0.51023 | 0.541 | 0.57328 | 0.60754 | 0.64456 | 0.68561 | 0.73317 | 0.79374 | 0.93623
F | 74 | 0.15893 | 0.18494 | 0.21092 | 0.23692 | 0.26299 | 0.28918 | 0.31556 | 0.3422 | 0.36919 | 0.39661 | 0.42461 | 0.45331 | 0.48293 | 0.5137 | 0.54598 | 0.58024 | 0.61726 | 0.6583 | 0.70587 | 0.76644 | 0.90893
P | 75 | 0.13192 | 0.15793 | 0.18391 | 0.20991 | 0.23598 | 0.26217 | 0.28855 | 0.31519 | 0.34217 | 0.3696 | 0.39759 | 0.4263 | 0.45592 | 0.48669 | 0.51897 | 0.55323 | 0.59025 | 0.63129 | 0.67886 | 0.73942 | 0.88192
l | 76 | 0.10516 | 0.13117 | 0.15716 | 0.18316 | 0.20923 | 0.23542 | 0.2618 | 0.28844 | 0.31542 | 0.34285 | 0.37084 | 0.39955 | 0.42916 | 0.45994 | 0.49221 | 0.52648 | 0.5635 | 0.60454 | 0.6521 | 0.71267 | 0.85516
a | 77 | 0.078628 | 0.10464 | 0.13062 | 0.15662 | 0.18269 | 0.20888 | 0.23526 | 0.2619 | 0.28889 | 0.31631 | 0.34431 | 0.37301 | 0.40263 | 0.4334 | 0.46568 | 0.49994 | 0.53696 | 0.578 | 0.62557 | 0.68614 | 0.82863
n | 78 | 0.052281 | 0.078294 | 0.10428 | 0.13028 | 0.15635 | 0.18254 | 0.20892 | 0.23556 | 0.26254 | 0.28997 | 0.31796 | 0.34667 | 0.37628 | 0.40706 | 0.43933 | 0.4736 | 0.51061 | 0.55166 | 0.59922 | 0.65979 | 0.80228
i | 79 | 0.026085 | 0.052097 | 0.07808 | 0.10408 | 0.13015 | 0.15634 | 0.18272 | 0.20936 | 0.23634 | 0.26377 | 0.29176 | 0.32047 | 0.35009 | 0.38086 | 0.41313 | 0.4474 | 0.48442 | 0.52546 | 0.57303 | 0.63359 | 0.77608
g | 80 | 0 | 0.026012 | 0.051996 | 0.077996 | 0.10406 | 0.13026 | 0.15663 | 0.18327 | 0.21026 | 0.23768 | 0.26568 | 0.29439 | 0.324 | 0.35477 | 0.38705 | 0.42132 | 0.45833 | 0.49938 | 0.54694 | 0.60751 | 0.75
i
r | 81 |  | 0 | 0.025983 | 0.051983 | 0.078051 | 0.10424 | 0.13062 | 0.15726 | 0.18424 | 0.21167 | 0.23967 | 0.26837 | 0.29799 | 0.32876 | 0.36104 | 0.3953 | 0.43232 | 0.47336 | 0.52093 | 0.5815 | 0.72399
O | 82 |  |  | 0 | 0.026 | 0.052068 | 0.07826 | 0.10464 | 0.13128 | 0.15826 | 0.18569 | 0.21368 | 0.24239 | 0.27201 | 0.30278 | 0.33505 | 0.36932 | 0.40634 | 0.44738 | 0.49495 | 0.55551 | 0.698
| 83 |  |  |  | 0 | 0.026068 | 0.05226 | 0.078639 | 0.10528 | 0.13226 | 0.15969 | 0.18768 | 0.21639 | 0.24601 | 0.27678 | 0.30905 | 0.34332 | 0.38034 | 0.42138 | 0.46895 | 0.52951 | 0.672
| 84 |  |  |  |  | 0 | 0.026192 | 0.052571 | 0.07921 | 0.10619 | 0.13362 | 0.16161 | 0.19032 | 0.21994 | 0.25071 | 0.28298 | 0.31725 | 0.35427 | 0.39531 | 0.44288 | 0.50344 | 0.64594
| 85 | [5 empty] | 0 | 0.026379 | 0.053018 | 0.080002 | 0.10743 | 0.13542 | 0.16413 | 0.19375 | 0.22452 | 0.25679 | 0.29106 | 0.32808 | 0.36912 | 0.41669 | 0.47725 | 0.61974
| 86 | [6 empty] | 0 | 0.026639 | 0.053622 | 0.08105 | 0.10904 | 0.13775 | 0.16737 | 0.19814 | 0.23041 | 0.26468 | 0.3017 | 0.34274 | 0.39031 | 0.45087 | 0.59337
| 87 | [7 empty] | 0 | 0.026983 | 0.054411 | 0.082404 | 0.11111 | 0.14073 | 0.1715 | 0.20377 | 0.23804 | 0.27506 | 0.3161 | 0.36367 | 0.42423 | 0.56673
| 88 | [8 empty] | 0 | 0.027428 | 0.055421 | 0.084129 | 0.11374 | 0.14452 | 0.17679 | 0.21106 | 0.24808 | 0.28912 | 0.33668 | 0.39725 | 0.53974
| 89 | 89: 0; 90: 0.027993; 91: 0.056702; 92: 0.086317; 93: 0.11709; 94: 0.14936; 95: 0.18363; 96: 0.22065; 97: 0.26169; 98: 0.30926; 99: 0.36982; 100: 0.51232
| 90 | 90: 0; 91: 0.028709; 92: 0.058324; 93: 0.089097; 94: 0.12137; 95: 0.15564; 96: 0.19266; 97: 0.2337; 98: 0.28126; 99: 0.34183; 100: 0.48432
| 91 | 91: 0; 92: 0.029615; 93: 0.060388; 94: 0.092662; 95: 0.12693; 96: 0.16395; 97: 0.20499; 98: 0.25255; 99: 0.31312; 100: 0.45561
| 92 | 92: 0; 93: 0.030773; 94: 0.063047; 95: 0.097314; 96: 0.13433; 97: 0.17537; 98: 0.22294; 99: 0.28351; 100: 0.426
| 93 | 93: 0; 94: 0.032274; 95: 0.066541; 96: 0.10356; 97: 0.1446; 98: 0.19217; 99: 0.25273; 100: 0.39523
| 94 | 94: 0; 95: 0.034267; 96: 0.071285; 97: 0.11233; 98: 0.15989; 99: 0.22046; 100: 0.36295
| 95 | 95: 0; 96: 0.037017; 97: 0.07806; 98: 0.12563; 99: 0.18619; 100: 0.32868
| 96 | 96: 0; 97: 0.041043; 98: 0.088608; 99: 0.14917; 100: 0.29167
| 97 | 97: 0; 98: 0.047565; 99: 0.10813; 100: 0.25062
| 98 | 98: 0; 99: 0.060566; 100: 0.20306
| 99 | 99: 0; 100: 0.14249
| 100 | 100: 0
Custom pf Calculator:
|  |  | Existing: | 72 |  | Desired: | 87 |  | kW: | 1430 |  |  | Enter data in these boxes only
|  |  | Factor: | 0.39713 |  |  |  | Req'd kVAR: | 567.8913
|  | 81: Old kVA:; 82: 1986.1111; 85: New kVA:; 86: 1643.6782 |  | 1430*0.397
|  |  | Old kVAR: | 1378.3096 | (to unity)